Electric Circuit 624 Overhead Rebuild

St. Charles Municipal Electric Utility is seeking an overhead line contractor to rebuild an existing single phase #6 Cu, 12kV circuit to 1/0 AL poly coated “tree” wire and rebuild the existing “open wire” secondary to 4/0 AL “Vicksburg” parallel lay.  The job also includes approximately 18 pole replacements, 7 overhead transformer replacements and installing new pole top pins and hardware to replace the existing construction.  The existing conductors can not be de-energized, so all work must be done hot.  The work is located between Fellows St. and Gray St., generally between S. 7th St. and S. 4th Street.

Proposals for Circuit 624 Rebuild, as described in the accompanying technical specification, shall be received before 10:00 a.m., Friday, March 28, 2014, at the City of St. Charles City Hall, Two East Main Street, St. Charles, IL 60174, Council Chambers, Attention: Tom Bruhl, P.E., Public Works – Electric Utility.  Proposals will be read aloud at this time.  Any proposal received subsequent to the time specified will be promptly returned to the Contractor unopened.

Proposals shall be in a sealed envelope labeled with “Sealed Bid - Electric Circuit 624 Overhead Rebuild.”

Any questions shall be submitted to Steve Shroba (Engineer) via e-mail to the following e-mail addresses:

sshroba@stcharlesil.gov

Upon receipt of questions prior to March 7, 2014, the Contractor shall receive a reply e-mail acknowledging the receipt of the question.  Response to the question shall be as soon as practical.  Should the question result in a clarification that requires addenda, such addenda will be issued to all registered Contractors, via e-mail, as soon as practical.

Questions submitted after 7:00 a.m., March 7, 2014, shall not be acknowledged or answered.  Contractors shall take all necessary steps to propose questions prior to March 7.

City reserves the right to extend the due date.  Should an extension be necessary, communication of such shall be e-mailed to all registered Contractors.

Scope:

The line is approximately 2,100 linear of which 1,200’ linear feet of primary and 1,800 linear feet of secondary is to be replaced, 18 pole replacements, six (6) deadend installations, seven (7) overhead transformer stations to be replaced.

The majority of the line is not truck accessible and would require the services of a “backyard” machine that is the responsibility of the Contractor.  It is recommended that the Contractor should take care to walk the job prior to bidding.

The bids for the rebuild will be lump sum, not to exceed, pricing.

All material will be provided by the City.

The City requires hand ties and the skinning of the 1/0 AL poly coated “tree” wire.  The existing primary neutral will also be removed.

In general, insulators, arresters, and deadends shall be replaced.  As noted above, the following are estimated quantities of additional replacement items identified when the City walked the line:

- (18) – pole replacements.  Primary poles are generally 40’-2 and shall be replaced as close to the existing as is practical.  Poles with secondary voltage attachments only will be 35’-4 pole installations.  Streetlight poles are 35’-4.

- (7) – pole-mount transformer with accessories (cut-outs & arresters)

- (1,200 ft.) – new poly-coated 1/0 Hendrix “Tree” primary wire

- (1,800 ft.) – new poly-coated 4/0 “Vicksburg” parallel lay secondary wire

The Contractor is responsible for any traffic control and protection measures that are needed.  A City inspector will be making spot checks and any deficiencies must be addressed immediately.  The Contractor is responsible for reviewing the jobsite and quantifying the need for flaggers and building in any additional costs related to flaggers.

The rough schedule for the job is for award of job in the first week of May, and the job must be completed before November 1, 2014.

The Contractor may not start work before 7 AM weekdays, and must be off the line by 2:30 PM weekdays.  The City shall place the line on “non-reclosing” and “hot line tag” each day by 7:15 AM.  Contractor must state any special “Lockout/Tagout” procedures that they would require.  Should a Contractor fail to clear the line by 2:30 PM, the City shall reduce the total lump sum cost of the job for City overtime costs.  For every 15 minutes of City overtime needed, the lump sum job cost will be reduced at the rate of $190.50 per hour.

Once the work starts, the City expects, within reason, the work to proceed without delay to completion.  The City expects the work to take no more than eight weeks to complete.

The City will be providing an Inspector who will act as the single point of contact between the Contractor and the City.  The City Inspector should be able to interface and communicate with the Contractor during the normal crew work day.  The City expects the Contractor to communicate to the City on a daily basis with regard to the work plan and schedule.

Respect for the residents’ property is paramount.  Since installations will typically be in the back yards of City of St. Charles residents, please indicate if you utilize any type of notification system for property owners in the vicinity of where you will be working to let them know who you are, why you are there and what to do if they have a complaint.  The contractor will be required to use a “door-hanger” card or other communication means to notify property owners of work in their area.  This notification must identify the contractor name and also reference that you are doing work for the City of St. Charles Electric Utility.  A contact number must be included for each.  Notification to residents shall be made no earlier than 14 days prior to start of work, but must be at least three days prior to start of work.  Where specialized equipment could be utilized to minimize private property damage, Contractor should consider such.  Contractor shall identify in their bid any work on private property that may damage trees, landscaping, fences, sheds, or other.  Reasonable restoration of landscape required to complete the job will be performed by the City and shall not be required to be in the Contractor lump sum price.  Any abnormal damage, as deemed by the City Inspector, shall be the responsibility of the Contractor, without any additional payment by the City.  The amount of forecast damage in the Contractor’s bid, requiring City restoration, shall be added to the evaluated price.  To the extent that private property damage can be minimized, it is in the Contractor’s best interest.

All scrap wire and materials are the property of the City and shall be delivered to the City Public Works Compound in a coordinated meeting with the Inspector.  The City knows approximately the amount of scrap that will be generated, and any shortcoming of that will be held back from the final payment to the Contractor.

The Contractor shall provide a Safety Officer contact for the City Inspector to address any safety related concerns that arise on the job.  The Safety Officer shall have the ability to respond and address the concern in a timely fashion.

The City Public Works facility, upon request, can be used for a job show up location.  Utility trucks and private cars can be parked within our fenced-in yard.  The City reserves the right to revoke this privilege.  The yard is open weekdays from 6:00 a.m. to 5:30 p.m. and locked at all other times.

Job walk down for bidders:  If requested, the City will provide a job walk down starting at 9:00 a.m. on Tuesday, March 4.  Rain date at same time on March 5.  Those interested shall e-mail Gary Sittler at gsittler@stcharlesil.gov to make arrangements to attend this walk down and for the meeting location. This shall be the only opportunity to walk the job down with the City prior to the bid being due.

Attachments/supplemental drawings:

- Overview Aerial

- Overview Poles

This is an IBEW union job within Local 196 jurisdiction.

Lump Sum Price to Rebuild Circuit 624   $ ________________________

List of Private Property Damage Anticipated:

The City is requesting contractors provide additional loaded hourly crew rates in the event the City wishes to engage the contractor for other work, including emergency or restoration work during emergencies.

Additional work – straight time hourly rates

The City may choose to hire the Contractor on a time and material basis for additional projects.  Please provide a loaded crew rate for a standard overhead crew with standard equipment, assuming no flagging required.

$ ______________ per crew hour without flaggers

The City may choose to hire the Contractor on a time and material basis for additional projects.  Please provide a loaded crew rate for a standard overhead crew with standard equipment, including two flaggers in the event that the job is on a street where a lane is blocked.

$ ______________ per crew hour with flaggers

Additional work – Overtime at time and a half hourly rates

The City may choose to hire the Contractor on a time and material basis for additional projects.  Please provide a loaded crew rate for a standard overhead crew with standard equipment, assuming no flagging required, for overtime at time and a half, if such is part of your labor contract.

$ ______________ per crew hour without flaggers

The City may choose to hire the Contractor on a time and material basis for additional projects.  Please provide a loaded crew rate for a standard overhead crew with standard equipment, including two flaggers in the event that the job is on a street where a lane is blocked, for overtime at time and a half, if such is part of your labor contract.

$ ______________ per crew hour with flaggers

Additional work – Overtime at double time hourly rates

The City may choose to hire the Contractor on a time and material basis for additional projects.  Please provide a loaded crew rate for a standard overhead crew with standard equipment, assuming no flagging required, for overtime at double time, if such is part of your labor contract.

$ ______________ per crew hour without flaggers

The City may choose to hire the Contractor on a time and material basis for additional projects.  Please provide a loaded crew rate for a standard overhead crew with standard equipment, including two flaggers in the event that the job is on a street where a lane is blocked, for overtime at double time, if such is part of your labor contract.

$ ______________ per crew hour with flaggers

Feel free to provide additional pricing details or breakouts, or cost per hour for any specialized equipment.

Additional work – Traffic Control Flaggers

The City may choose to hire outside Contractors as flaggers only to assist in traffic control for additional projects not related to this Project.

$ ______________ per hour for two (2) flaggers

# Bid Evaluation

Bids will be evaluated on a weighted scale based on the following criteria (criteria not in any particular order):

- Ability of bidder to complete project within requested timeframe

- City experience with bidder regarding adherence to work schedules

- City experience with bidder regarding workmanship/quality

- City experience with bidder regarding responsiveness

- City experience with bidder regarding communication

- Evaluated cost

Special Terms and Conditions:

Work issued on the future purchase order resulting from this bid will be on an “as directed” basis.

Footage approximations are estimates only and are not a guaranteed quantity.

The City of St. Charles reserves the right to terminate any future purchase order resulting from this bid for convenience within 15 (fifteen) calendar days’ notice.